## Sheet1
Pressure at Critical Station Calculator
Calculator only applies to irrigation systems using plastic pipe.
Shaded Cells = Output Values
Pressure Available at Critical Station |  |  |  |  | Pressure Required at Critical Station
Pressure Available at POC | 80 |  |  |  | Valve PSI Loss | 3.6
Water Meter PSI Loss | 4.9 |  |  |  | Elevation at Critical Station (Feet) | 4835
Backflow Preventor PSI Loss | 7.5 |  |  |  | Elevation at Critical Emission Device (Feet) | 4840
Master Valve PSI Loss | 3.6 |  |  |  | PSI Change from Station to Critical Emission Device | -2.165
Flow Sensor PSI Loss | 0.95 |  |  |  | Lateral Line PSI Loss | 4.2582
Elevation at POC (Feet) | 4820 |  |  |  | Lateral Line PSI Table | Flow | Inner Diameter | Length | PSI Loss
Elevation at Critical Station (Feet) | 4835 |  |  |  | Lateral Line Segment 1 | 35 | 2.047 | 50 | 0.46894
PSI Change from POC to Station Due to Elevation | -6.495 |  |  |  | Lateral Line Segment 2 | 30 | 1.59 | 30 | 0.72322
Mainline PSI Loss | 4.5359 |  |  |  | Lateral Line Segment 3 | 22 | 1.59 | 40 | 0.54327
Mainline PSI Table | Flow | Inner Diameter | Length | PSI Loss | Lateral Line Segment 4 | 12 | 1.029 | 45 | 1.6545
Mainline Segment 1 | 50 | 2.047 | 250 | 4.5359 | Lateral Line Segment 5 | 8 | 1.029 | 50 | 0.86826
Mainline Segment 2 |  |  |  |  | Lateral Line Segment 6
Mainline Segment 3 |  |  |  |  | Lateral Line Segment 7
Mainline Segment 4 |  |  |  |  | Lateral Line Segment 8
Fittings PSI Loss (10%) | 0.45359 |  |  |  | Lateral Line Segment 9
Pressure Available (PSI) | 51.5655 |  |  |  | Fittings PSI Loss (10%) | 0.42582
[5 empty] | Critical Emission Device Operating Pressure | 30
[5 empty] | Pressure Required (PSI) | 40.449
[5 empty] | Residual Pressure Available (PSI) | 11.1166
If Residual Pressure Available (PSI) is a negative number, a booster pump may be required.